australian_network

Prepared using EPANET Hydraulic Analysis Toolkit

Engineer: Test Engineer

Date: 04 April 2026

Analysis per WSAA Guidelines

# Executive Summary

This report presents the hydraulic analysis of a water distribution network comprising 7 junctions, 9 pipes, 1 reservoir(s), and 1 tank(s). Analysis was performed in accordance with WSAA WSA 03-2011 guidelines for Australian water supply systems.

## Compliance Overview

3 WARNING(s) — Items requiring review and remediation.

8 informational item(s) noted (e.g., low velocity warnings).

## Key Hydraulic Metrics

| Metric | Value |
| --- | --- |
| Pressure Range | 17.2 – 41.6 m |
| WSAA Min (20 m) | FAIL |
| WSAA Max (50 m) | PASS |
| Max Velocity | 2.83 m/s (FAIL — limit 2.0 m/s) |

## Recommended Actions

Investigate low pressure at J4. Consider booster pump station or supply augmentation.

Review pipe sizing for P4, P8 — velocity exceeds WSAA 2.0 m/s limit. Consider upsizing or parallel main.

# 1. Network Description

## 1.1 Network Summary

| Component | Count |
| --- | --- |
| Junctions | 7 |
| Reservoirs | 1 |
| Tanks | 1 |
| Pipes | 9 |
| Valves | 0 |
| Pumps | 0 |
| Duration (hrs) | 24.0 |

# 2. Steady-State Results

## 2.1 Junction Pressures

| Junction | Min (m) | Max (m) | Avg (m) |
| --- | --- | --- | --- |
| J1 | 26.4 | 29.9 | 29.4 |
| J2 | 31.1 | 34.8 | 33.6 |
| J3 | 33.1 | 37.8 | 35.9 |
| J4 | 17.2 | 31.9 | 30.9 |
| J5 | 34.2 | 39.7 | 37.5 |
| J6 | 34.4 | 41.6 | 38.8 |
| J7 | 31.1 | 35.8 | 33.9 |

## 2.2 Pipe Flows

| Pipe | Min (LPS) | Max (LPS) | Avg (LPS) | Velocity (m/s) |
| --- | --- | --- | --- | --- |
| P1 | 11.4 | 106.41 | 36.02 | 0.51 |
| P2 | 10.5 | 52.5 | 29.96 | 0.61 |
| P3 | 5.78 | 28.91 | 16.5 | 0.53 |
| P4 | 0.9 | 88.91 | 6.06 | 0.19 |
| P5 | 3.38 | 16.91 | 9.65 | 0.31 |
| P6 | 1.8 | 9.0 | 5.14 | 0.29 |
| P7 | 3.22 | 16.09 | 9.18 | 0.52 |
| P8 | 0.0 | 87.41 | 3.5 | 0.11 |
| P9 | -10.09 | -2.02 | -5.76 | 0.33 |

Steady-state analysis completed for 7 junctions and 9 pipes. See compliance section for detailed checks.

# 3. Compliance Summary

The following compliance checks have been performed against Australian standards (WSAA Guidelines).

| Status | Element | Message |
| --- | --- | --- |
| WARNING | J4 | Min pressure 17.2m < 20m (WSAA minimum) |
| INFO | P1 | Low velocity 0.51 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P3 | Low velocity 0.53 m/s < 0.6 m/s (sediment risk — WSAA) |
| WARNING | P4 | Velocity 2.83 m/s > 2.0 m/s limit |
| INFO | P4 | Low velocity 0.19 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P5 | Low velocity 0.31 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P6 | Low velocity 0.29 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P7 | Low velocity 0.52 m/s < 0.6 m/s (sediment risk — WSAA) |
| WARNING | P8 | Velocity 2.78 m/s > 2.0 m/s limit |
| INFO | P8 | Low velocity 0.11 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P9 | Low velocity 0.33 m/s < 0.6 m/s (sediment risk — WSAA) |

# Conclusions

3 warning(s) were identified. These should be reviewed and addressed where practicable to improve network performance.