Brisbane 50-Lot Subdivision — Fire Flow Assessment

Prepared using EPANET Hydraulic Analysis Toolkit

Engineer: Design Engineer

Date: 06 April 2026

Analysis per WSAA Guidelines

# Executive Summary

This report presents the hydraulic analysis of a water distribution network comprising 13 junctions, 17 pipes, 1 reservoir(s), and 0 tank(s). Analysis was performed in accordance with WSAA WSA 03-2011 guidelines for Australian water supply systems.

## Compliance Overview

1 WARNING(s) — Items requiring review and remediation.

## Key Hydraulic Metrics

| Metric | Value |
| --- | --- |
| Pressure Range | 33.3 – 39.6 m |
| WSAA Min (20 m) | PASS |
| WSAA Max (50 m) | PASS |
| Max Velocity | 2.64 m/s (FAIL — limit 2.0 m/s) |

## Recommended Actions

Review pipe sizing for P17 — velocity exceeds WSAA 2.0 m/s limit. Consider upsizing or parallel main.

# 1. Network Description

## 1.1 Network Summary

| Component | Count |
| --- | --- |
| Junctions | 13 |
| Reservoirs | 1 |
| Tanks | 0 |
| Pipes | 17 |
| Valves | 0 |
| Pumps | 0 |
| Duration (hrs) | 0.0 |

# 2. Steady-State Results

## 2.1 Junction Pressures

| Junction | Min (m) | Max (m) | Avg (m) |
| --- | --- | --- | --- |
| J1 | 33.3 | 33.3 | 33.3 |
| J2 | 34.9 | 34.9 | 34.9 |
| J3 | 36.7 | 36.7 | 36.7 |
| J4 | 34.0 | 34.0 | 34.0 |
| J5 | 35.7 | 35.7 | 35.7 |
| J6 | 37.5 | 37.5 | 37.5 |
| J7 | 34.8 | 34.8 | 34.8 |
| J8 | 36.6 | 36.6 | 36.6 |
| J9 | 38.2 | 38.2 | 38.2 |
| J10 | 35.4 | 35.4 | 35.4 |
| J11 | 37.2 | 37.2 | 37.2 |
| J12 | 39.6 | 39.6 | 39.6 |
| J13 | 37.2 | 37.2 | 37.2 |

## 2.2 Pipe Flows

| Pipe | Min (LPS) | Max (LPS) | Avg (LPS) | Velocity (m/s) |
| --- | --- | --- | --- | --- |
| P1 | 26.08 | 26.08 | 26.08 | - |
| P2 | 12.77 | 12.77 | 12.77 | - |
| P3 | 9.12 | 9.12 | 9.12 | - |
| P4 | 13.24 | 13.24 | 13.24 | - |
| P5 | 9.14 | 9.14 | 9.14 | - |
| P6 | 9.02 | 9.02 | 9.02 | - |
| P7 | 13.07 | 13.07 | 13.07 | - |
| P8 | 9.06 | 9.06 | 9.06 | - |
| P9 | 12.08 | 12.08 | 12.08 | - |
| P10 | 3.46 | 3.46 | 3.46 | - |
| P11 | 4.03 | 4.03 | 4.03 | - |
| P12 | 4.16 | 4.16 | 4.16 | - |
| P13 | 3.16 | 3.16 | 3.16 | - |
| P14 | 0.04 | 0.04 | 0.04 | - |
| P15 | 0.04 | 0.04 | 0.04 | - |
| P16 | 0.04 | 0.04 | 0.04 | - |
| P17 | 25.07 | 25.07 | 25.07 | - |

Steady-state analysis completed for 13 junctions and 17 pipes. See compliance section for detailed checks.

# 3. Compliance Summary

The following compliance checks have been performed against Australian standards (WSAA Guidelines).

| Status | Element | Message |
| --- | --- | --- |
| WARNING | P17 | Velocity 2.64 m/s > 2.0 m/s limit |

# Conclusions

1 warning(s) were identified. These should be reviewed and addressed where practicable to improve network performance.