network

Prepared using EPANET Hydraulic Analysis Toolkit

Date: 06 April 2026

Analysis per WSAA Guidelines

# Executive Summary

This report presents the hydraulic analysis of a water distribution network comprising 10 junctions, 11 pipes, 1 reservoir(s), and 0 tank(s). Analysis was performed in accordance with WSAA WSA 03-2011 guidelines for Australian water supply systems.

## Compliance Overview

3 WARNING(s) — Items requiring review and remediation.

7 informational item(s) noted (e.g., low velocity warnings).

## Key Hydraulic Metrics

| Metric | Value |
| --- | --- |
| Pressure Range | 11.2 – 44.6 m |
| WSAA Min (20 m) | FAIL |
| WSAA Max (50 m) | PASS |
| Max Velocity | 2.29 m/s (FAIL — limit 2.0 m/s) |

## Recommended Actions

Investigate low pressure at J9, J10. Consider booster pump station or supply augmentation.

Review pipe sizing for P10 — velocity exceeds WSAA 2.0 m/s limit. Consider upsizing or parallel main.

# 1. Network Description

## 1.1 Network Summary

| Component | Count |
| --- | --- |
| Junctions | 10 |
| Reservoirs | 1 |
| Tanks | 0 |
| Pipes | 11 |
| Valves | 0 |
| Pumps | 0 |
| Duration (hrs) | 0.0 |

# 2. Steady-State Results

## 2.1 Junction Pressures

| Junction | Min (m) | Max (m) | Avg (m) |
| --- | --- | --- | --- |
| J1 | 44.6 | 44.6 | 44.6 |
| J2 | 41.1 | 41.1 | 41.1 |
| J3 | 38.8 | 38.8 | 38.8 |
| J4 | 33.7 | 33.7 | 33.7 |
| J5 | 28.6 | 28.6 | 28.6 |
| J6 | 30.7 | 30.7 | 30.7 |
| J7 | 37.0 | 37.0 | 37.0 |
| J8 | 43.2 | 43.2 | 43.2 |
| J9 | 16.1 | 16.1 | 16.1 |
| J10 | 11.2 | 11.2 | 11.2 |

## 2.2 Pipe Flows

| Pipe | Min (LPS) | Max (LPS) | Avg (LPS) | Velocity (m/s) |
| --- | --- | --- | --- | --- |
| P1 | 55.0 | 55.0 | 55.0 | 0.78 |
| P2 | 35.14 | 35.14 | 35.14 | 0.72 |
| P3 | 31.14 | 31.14 | 31.14 | 0.63 |
| P4 | 7.14 | 7.14 | 7.14 | 0.23 |
| P5 | 4.14 | 4.14 | 4.14 | 0.23 |
| P6 | -3.86 | -3.86 | -3.86 | 0.22 |
| P7 | -6.86 | -6.86 | -6.86 | 0.39 |
| P8 | -11.86 | -11.86 | -11.86 | 0.38 |
| P9 | -14.86 | -14.86 | -14.86 | 0.47 |
| P10 | 18.0 | 18.0 | 18.0 | 2.29 |
| P11 | 4.0 | 4.0 | 4.0 | 0.51 |

Steady-state analysis completed for 10 junctions and 11 pipes. See compliance section for detailed checks.

# 3. Compliance Summary

The following compliance checks have been performed against Australian standards (WSAA Guidelines).

| Status | Element | Message |
| --- | --- | --- |
| WARNING | J9 | Min pressure 16.1m < 20m (WSAA minimum) |
| WARNING | J10 | Min pressure 11.2m < 20m (WSAA minimum) |
| INFO | P4 | Low velocity 0.23 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P5 | Low velocity 0.23 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P6 | Low velocity 0.22 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P7 | Low velocity 0.39 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P8 | Low velocity 0.38 m/s < 0.6 m/s (sediment risk — WSAA) |
| INFO | P9 | Low velocity 0.47 m/s < 0.6 m/s (sediment risk — WSAA) |
| WARNING | P10 | Velocity 2.29 m/s > 2.0 m/s limit |
| INFO | P11 | Low velocity 0.51 m/s < 0.6 m/s (sediment risk — WSAA) |

# Conclusions

3 warning(s) were identified. These should be reviewed and addressed where practicable to improve network performance.